## DOOR AUDIT
Annual Full Door Audit
A full door audit was undertaken to check that all doors are closing effectively, paying attention to all intumescent strips, door closing devices, hinges, glazing and ironmongery. Check is carried each year or when the building works are performed that may affect the fire fighting integrity of the doors. Remedial action must be recorded in the Fire Action Plan.
Door Location | Fire Door Labelling Present? | Fire Door Gaps & Seals | Door Hinges & Closers | Fire Door Glass & Glazing | Fire Door Leaf, Frame and Operation | Lock Mechanisms Present? | Fire Door Retainer Present?
Completed by:
Position:
Date Checked:
Signature:
Note on B6: Stephen Ross: • Look for a label, a plug or a similar marking on the top (or occasionally on the side) of the door to show that it’s certiﬁcated, and follow the instructions. IMPORTANT: All ironmongery such as locks, latches, closers and hinges, MUST be CE marked and compatible with the door set’s certiﬁcation • Without a certiﬁcation mark, you cannot be sure this really is a ﬁre door • Use a mirror or the camera on your phone. Or, better still, a Checkmate Fire GAP Gauge.
Note on C6: Stephen Ross: • Look for any intumescent seals around the doorframe or leaf edge. Check they’re intact with no sign of damage. Check the gap around the door frame/leaf edge is constant and less then 4mm when the door is closed. The gap under the door can be slightly larger (up to 10mm) unless it’s a ﬁre/smoke door, in which case it should also be less than 4mm - but it does depend on the door. • All seals should be from the same manufacturer and not diﬀerent speciﬁcations. A clue would be to observe seals of diﬀerent colours, or a combination of brush and ﬁn seals in the same door set.
Note on D6: Stephen Ross: • Check that the closer shuts the door into closed position - and that CE marked grade 11 or 13 hinges are ﬁrmly ﬁxed (3 or more of them), with no missing screws • Be sure the door has been properly maintained - check for any maintenance or remediation events which have been carried out to the door.
Note on E6: Stephen Ross: • Check the seal is continuous and present between the glass and beading. Also, check that the glazing beads are ﬁrmly ﬁxed to the glazing aperture and free from damage • Be sure the seals, beads and glass are all intact and free from damage to ensure they will work in the event of a ﬁre. Clear glass should display manufacturer and FR performance marks etched in the top or bottom corner or the glass.
Note on F6: Stephen Ross: • Check the door leaf closes ﬁrmly onto the frame without binding. This can be a sign of a poorly installed door set • A ﬁre door only works when it’s closed. A ﬁre door is rendered completely useless if it’s wedged open or can’t close fully.
Note on G6: Stephen Ross: • Whats ironmongery is presents, locks, pushbars, ceramic dead bolts, key locks, push pads etc.
Note on H6: Stephen Ross: • Check the door for installed safety equipment such as magnetic contacts or dorgards.